## schedule
COMPLETION OF COFFEE ANALYTICAL LABORATORY &REGIONAL OFFICE AT RUKOKI IN KASESE
MECHANICAL INSTALLATION - SCHEDULE OF MATERIALS
Item | Description | Photograph
SANITARY FITIINGS
WC TYPE 1
A | Roca WC suite with horizontal outlet as ROCA No. 342395.0 complete with 3/6Litre dual flush cistern fitting, internal overflow, plastic seat and cover with stainless steel hinges.
WC TYPE 2
B | Squatting type WC pan as ROCA Oriental No.345090001, with bottom outlet, exposed flush valve as specified.
C | Roca Handcap WC suite with horizontal outlet No. 527003010 fixing kit complete with 3/6 Litre dual flush cistern, internal overflow, plastic seat and cover with stainless steel hinges, and a set of grab rails, wash basin, toilet paper holder, and frameless mirror as approved.
WASH BASIN
D | ROCA JAVA Countertop No. 327863.0, 475mm counter top basin complete with Roca Modena monoblock basin mixer with aerator, pop-up waste, flexible supply hoses, and filters, CP waste and bottle trap.
E | ROCA JAVA wall hang wash hand basin complete with Roca Modena monoblock basin mixer with aerator, pop-up waste, flexible supply hoses, and filters, CP waste and bottle trap.
SHOWER HEAD
E | Basic shower head complete with arm and control valve
TOILET ROLL HOLDER
F | ROCA SUPERINOX as No. 81568300Y in stainless steel finish
BOWL URINAL
A | ROCA SITE urinal set with one bowl for one person No. 359601000 complete with built-in water supply with fixing set, waste pipe, flexible tube, elbow joint and connector and plastic bottle trap.
WC FLUSH VALVE
B | ROCA WC concealed flush valve as Aqua No. 506902810 with round tray
URINAL FLUSH VALVES
C | ROCA URINAL flush valve with straight discharge pipe as ROCA Gem No. 526900710
SHOWER TRAY
D | Franke Model LDS Drip Sink 600 x 500 x 258mm deep, manufactured from Grade 304 (18/10) Stainless Steel, complete with Stainless Steel hinged bucket grid. Unit fitted on to one pair of Stainless Steel Falcon brackets to wall and provision for 40mm waste outlet. Unit to be fitted 600mm from finished floor level.
COAT HOOK
E | ROCA DOUBLE ROBE HOOK FASHION No. 815491001 in stainless steel finish
STAINLESS STEEL SINK TYPE 1
F | To be Single Bowl Single Drain as ROCA SERIE E E-135 - 870440803 size 800x500mm with two deck pattern sink mixers 306-998.008, brackets, slotted waste 40mm and chrome plated bottle p trap.
STAINLESS STEEL SINK TYPE 2
A | To be Double Bowl double Drain as ROCA SERIE E E-1901 - 870481803 size 1800x500mm with two deck pattern sink mixers 306-998.008, brackets, slotted wastes 40mm and chrome plated bottle p trap.
MIRROR
B | Frameless polished edge with dome shaped chrome plated screws
SOAP DISPENSER
C | Approved plunger type soap dispenser in stainless steel casing
SOAP HOLDER
E | ROCA Dobla Built-in soap holder as No. 390407001
TOWEL RAIL
F | ROCA Superinox No. 81568700Y
FIRE FIGHTING EQUIPMENT
CARBON DIOXIDE FIRE EXTINGUISHER
A | 5 Kg carbon dioxide extinguisher in metal casing with lever and swivel arm to B.S. 5423 as ANGUS complete with seal, label and fixing brackets.
POWDER TYPE FIRE EXTINGUISHER
B | 6kg dry powder fire extinguisher in metal casing as ANGUS ABC all purpose powder complete with seal, label and brackets to BS 5423.
HOSE REEL
D | Swinging type to BS 5274 as Angus model 5 with 19mm dia. bore, 30 metre long hose with nylon jet/spray/off nozzle, capable of withstanding a pressure of 10 bar. To be complete with 20mm shut off valve, and with approved lettering and colour, complete with Cabinet as ANGUS MJ32119313 Double Door size:800(W)x1600(H)x300(D)mm to house the hosereel and the fire extinguisher. To be in stainless steel finish
FIRE HYDRANT
E | To be mounted near the entrance area . The stand pipe is to BS 44940 with 2no. globe valves 65mm dia.. and with instantaneous female coupling adapters.

## Plumbing
COMPLETION OF COFFEE ANALYTICAL LABARATORY & REGIONAL OFFICE IN RUKOKI - KASESE
MECHANICAL INSTALLATION - BILL OF QUANTITIES
Item | Description & Specification | Unit | Qty | Rate (UGX) | Amount (UGX)
WATER SUPPLY
The Contractor shall supply, install, test and commission to the satisfaction of the Engineer the following works including all necessary fixing/mounting accessories and builders' works
A | PN 16 PPR 50mm pipes in wall chase and below work benches complete with all necessary fittings and clamps and including builders works | m | 46
B | Ditto but 40mm | m | 20
C | Ditto but 32mm | m | 80
D | Ditto but 25mm | m | 60
E | Control valves size 50mm as per drawings | No. | 2
TOTAL TO COLLECTION
SANITARY FITTINGS
The Contractor shall supply, install, connect to existing and make ready for use including clamps and fittings and making good builder's works the following as per drawings
A | WC suite Sitting type complete with 3/6Litre dual flush cistern fitting, internal overflow, plastic seat,horizontal outlet and cover with stainless steel hinges as ROCA or equal and approved . | No. | 8
B | WC suite Squatting type complete as ROCA Oriental No.345090001, with bottom outlet, exposed flush valve or Equal &Approved | No. | 5
C | Ditto but WC suite for the disabled complete as specified on drawings : | No. | 1
D | Bowl urinal complete with built-in water supply with fixing set, waste pipe, flexible tube, elbow joint and connector and plastic bottle trap complete as ROCA or equal and approved. | No. | 4
E | Counter top Wash basin complete with Roca Modena monoblock basin mixer with aerator, pop-up waste, flexible supply hoses, and filters, CP waste and bottle trap as ROCA JAVA Countertop No. 327863 or equal and approved | No. | 12
F | Ditto but wall hang wash hand basin complete with Modena monoblock basin mixer with aerator, pop-up waste, flexible supply hoses, and filters, CP waste and bottle trap as ROCA JAVA or equal and approved | No. | 3
F | Kitchen sink Single Bowl Single Drain size 800x500mm with two deck pattern sink mixers brackets, slotted waste 40mm and chrome plated bottle p trapas as ROCA or equal and approved | No. | 1
| Laboratory sink Double Bowl size 1800x500mm ,double Drain complete with two deck pattern sink mixers, brackets, slotted wastes 40mm and chrome plated bottle p trap as ROCA or equal and approved | No. | 3
G | Basic shower head complete with arm and control valve. | No. | 2 |  | 0
H | Frameless mirror size 1200 x 700mm polished edge with dome shaped chrome plated screws. | No. | 7
I | Coat hook as specified | No. | 15
J | Flexible connectors | No. | 28
K | CP point of use isolating valve 15mm | No | 28
L | Toilet roll holders complete in stainless steel finish as ROCA or equal and approved. | No. | 15
M | Soap dispenser complete in stainless steel casing as Plunger type or equal and approved | No. | 10
N | Automatic hand drier complete as specified | No. | 8
O | Toilet brush complete as specified | No. | 15
TOTAL TO COLLECTION
DRAINAGE SYSTEM - PIPES AND FITTINGS
All pipes and fittings are to Terrain manufacture unless otherwise specified. The pipes and fittings are to be fitted complete with all necessary fittings and accessories including bends, tees, clamps and all builders work
A | PN 10 uPVC drain pipe 110mm diam as no. 100.4.40 laid in floor slab and in ducts | m | 102
B | Ditto but 50mm diam as no. 200.2.40 | m | 162
C | Ditto but 40mm diam as no. 200.15.40 | m | 108
D | WC connector as no. 128.4.02 | No. | 10
E | Trapped floor gully | No. | 23
F | Outside gully trap built in concrete complete with grating, gully piece, and P-trap | No | 13
TOTAL TO COLLECTION
GENERAL WORKS
WATER SUPPLY, STORAGE AND DISTRIBUTION
The Contractor shall supply, install, test and commission to the satisfaction of the Engineer the following including all the necessary fittings and builders' works
A | Excavate trench fill ram and cart away excess soil to lay supply pipes trench size 900X1000mm deep | m | 220
B | Inline stainer 25mm | No | 1
C | Non return valve 32mm | No | 1
D | Control valves for cold water pipes, size 50mm as per drawings | No. | 3
E | Ditto but 32mm as per drawings | No. | 3
F | Ditto but 25mm as per drawings | No. | 4
G | Smart stainless water storage tanks capacity 5000 litres size complete with cover, inlet, outlet, overflow, washout float to be installed at roof terrace | No | 2
H | Ditto but 2000 litres for Fire hose reel system | No | 1
I | Allow for NWSC connection to site complete with new meter | item | 1
J | PN 16 PPR 50mm distribution pipe complete with all necessary fittings, clamps laid from the tank area through the ceiling to the respective ducts and drop points as per the drawings | m | 52
K | Ditto but 32mm | m | 18
L | Valve chamber in concrete surround with cover 450x300mm | No | 2
M | Stand pipes in 20mm HDPE as convinnient points as per the landscape designs | No | 2
N | Fire hydrant outlets complete with control valves | No | 2
O | 65mm HDPE pipe laid in ground for fire hydrant line c/w all bends, connectors and other accessories | LM | 170
RAIN WATER DISPOSAL
P | 110mm diameter uPVC down pipe: Clipped to walls | LM | 144
Q | Extra over outlet to suit 110mm diameter pipe. | NO | 6
R | Extra over for shoe | NO | 6
S | Allow for testing and commissioning of water supply and distribution system including all sanitary fittings | Item | 1
TOTAL TO COLLECTION
GENERAL WORKS (Cont'd)
DRAINAGE SYSTEM - PIPES AND FITTINGS
All pipes and fittings are to Terrain manufacture unless otherwise specified. The pipes and fittings are to be fitted complete with all necessary fittings and accessories including clamps and all builders work
A | Excavate trench fill ram and cart away excess soil to lay drain pipes trench size 600 wide, to depth as per site invert levels | m | 180
B | uPVC drain pipe 150mm diam PN 10 laid in trench | m | 140
C | Ditto but 110mm | m | 96
D | Excavate for and construct manhole size 450 x 600mm and not exceeding 1m deep including channels, benching and providing medium duty ceramic manhole in green areas and heavy duty cast iron covers with frame in drive ways all to Engineer's detail | No | 14
E | Ditto but 1.5m deep | No | 8
G | Vent cowl 110mm | No. | 4
I | Allow construction of 100 user septic tank complete with soak pit as to structural engineer's details | Item | 1
J | Allow for testing and commissioning of the drainage system | Item | 1
TOTAL TO COLLECTION
GENERAL WORKS COLLECTION
PAGE M09
PAGE M10
TOTAL TO COLLECTION
COLLECTION
WATER SUPPLY
SANITARY FITTINGS
DRAINAGE SYSTEM (PIPES AND FITTINGS)
GENERAL WORKS
P-T | TOTAL FOR PLUMBING INSTALLATION

## Fire fighting
COMPLETION OF COFFEE ANALYTICAL LABARATORY & REGIONAL OFFICE IN RUKOKI - KASESE
MECHANICAL INSTALLATION - BILL OF QUANTITIES
Item | Description & Specification | Unit | Qty | Rate (UGX) | Amount (UGX)
FIRE FIGHTING
The Contractor shall supply, install, test and commission to the satisfaction of the Engineer the following works including all necessary fixing/mounting accessories and builders' works
A | Hosereel pump as Grundfoss capacity 2Cum/Hr at 30m head 1ph, 240V, 0.55kW complete with a weather proof control panel, bypass, pressure switch, gauge, pressure tank and all necessary accessories | No | 1
B | Inline stainer 50mm | No | 1
C | Non return valve 50mm | No | 1
D | Class C GI pipe size 50mm in walls and ducts | m | 22
E | Ditto but size 25mm | m | 38
F | Fire hydrant outlets complete with all accessories | No. | 2
G | Wall mounted swinging type hose reel with 30m long hose complete with cabinet as specified | No. | 3
H | 5 Kg carbon dioxide extinguisher in metal casing with lever and swivel arm complete with seal, label and fixing brackets as ANGUS or equal and approved | No | 5
I | 6kg Dry powder fire extinguisher in metal casing all purpose powder complete with seal, label and brackets as ANGUS ABC or equal and approved. | No | 5
FF-T | TOTAL TO COLLECTION

## HVAC
COMPLETION OF COFFEE ANALYTICAL LABARATORY & REGIONAL OFFICE IN RUKOKI - KASESE
MECHANICAL INSTALLATION - BILL OF QUANTITIES
Item | Description & Specification | Unit | Qty | Rate (UGX) | Amount (UGX)
AIR CONDITIONING INSTALLATION
The Contractor shall supply, install, test and commission to the satisfaction of the Engineer the following works including all necessary fixing/mounting accessories and builders' works
GROUND FLOOR
A | MULTI V5 outdoor unit cooling capacity 197,000 btu/hr (58kW), power input 3ph, 415V as to LG or approved equivalent. The unit shall be installed complete with power connection from a board(DB-G) on Ground Floor. The unit shall be complete with Sollatek automatic voltage switch or equal and approved.(Located at roof terrace) | No. | 1
B | Indoor 4-way ceiling casettes units as LG or equal and approved of cooling Capacity 24000btu/hr (7.1kW) complete with built in drain - up pump, drain hose, clamp metal, sound absorbing thermal insulation as Polyurethane form for fitting, wireless remote controller as c/w all other accessories. | No. | 4
C | Ditto but with Cooling Capacity: 18000 btu/hr (5.6kW) | No. | 4
Refrigerant piping as Daikin multi interlocking or equal and approved including insulation and supports
D | 12.7/26.6mm | m | 8
E | 12.7/22.2mm | m | 22
F | 9.5/19.1mm | m | 8
G | 9.5/15.9mm | m | 16
H | 6.4/12.7mm | m | 26
Refnet Joints (Liquid/Gas Sets)
I | Refnet joint (assorted) | No | 8
J | Poly vinyl sheathed inter wiring cable 2.5mmSq Cable to be wired to all indoor units and finally to central remote controller | item | 1
K | LCD central remote controller as LG PACS4B000 | No. | 1
Drainage from indoor units
L | 32mm uPVC drain pipe c/w all fixtures and terminated to a nearby storm water drain | M | 28
M | Ditto but 25mm | M | 42
N | Ceiling Mounted Fans as S&P or approved equivalent Hi-Line Sweep Fan 1.5m sweep diameter, 7kg weight, speed 12,600m3/hr complete with wall mounted switch and all necessary accessories | No. | 5
AC-1 | TOTAL TO COLLECTION
FIRST FLOOR
A | MULTI V5 outdoor unit cooling capacity 197,000 btu/hr (58kW), power input 3ph, 415V as to LG or approved equivalent. The unit shall be installed complete with power connection from a board(DB-G) on Ground Floor. The unit shall be complete with Sollatek automatic voltage switch or equal and approved.(Located at roof terrace) | No. | 1
B | Indoor 4-way ceiling casettes units as LG or equal and approved of cooling Capacity 24000btu/hr (7.1kW) complete with built in drain - up pump, drain hose, clamp metal, sound absorbing thermal insulation as Polyurethane form for fitting, wireless remote controller as c/w all other accessories. | No. | 1
C | Ditto but with Cooling Capacity: 18000 btu/hr (5.6kW) | No. | 4
D | Ditto but with Cooling Capacity: 12000 btu/hr (3.6kW) | No. | 1
E | Wall mounted indoor unit of cooling capacity 12000 btu/hr(3.6kW) as LG or approved equivalent for the server room connected on the VRF system | No. | 1
F | Ditto but split unit system c/w outdoor unit located on roof terrace. System complete with refrigerant pipe, AVS power regulator and all other necessary accessories (standby system for server room) | set | 1
Refrigerant piping as toshiba multi interlocking or equal and approved including insulation and supports
G | 12.7/22.2mm | m | 12
H | 9.5/19.1mm | m | 14
I | 9.5/15.9mm | m | 18
J | 6.4/12.7mm | m | 32
Refnet Joints (Liquid/Gas Sets)
K | Refnet joint (assorted) | No | 8
L | Poly vinyl sheathed inter wiring cable 2.5mmSq Cable to be wired to all indoor units and finally to central remote controller | item | 1
Drainage from indoor units
M | 40mm uPVC drain pipe c/w all fixtures and terminated to a nearby storm water drain | M | 10
N | Ditto but 32mm | M | 22
O | Ditto but 25mm | M | 36
P | Ceiling Mounted Fans as S&P or approved equivalent Hi-Line Sweep Fan 1.5m sweep diameter, 7kg weight, speed 12,600m3/hr complete with wall mounted switch and all necessary accessories | No. | 2
Q | Allow for mechanical extraction/ventilation of the chemical anlysis room complete with 375x375 extract grille, duct work, control damper, and outdoor extract fan at roof terrace. All the necessary accessories and controls to be considered, all to the satisfaction of the supervising mechanical engineer | item | 1
R | Allow for testing and commissioning of the HVAC system | item | 1
AC-2 | TOTAL TO COLLECTION
COLLECTION PAGE FOR HVAC WORKS
GROUND FLOOR PAGE AC-1
FIRST FLOOR PAGE AC-2
VAC-T | TOTAL FOR HVAC TO MAIN COLLECTION PAGE

## Risk work (hidden)
REMODELLING AND DEVELOPING OF NEW CHURCH EXTENSION IN WALUKUBA FOR CHURCH OF JESUS CHRIST OF LATTER DAY SAINTS
MECHANICAL INSTALLATION - BILL OF QUANTITIES (Risk Work)
DWG NO. MKK307D/ M1-M4, AC1
Item | Description & Specification | Unit | Qty | Rate (UGX) | Amount (UGX)
RISK WORKS
WATER SUPPLY, STORAGE AND DISTRIBUTION
The Contractor shall supply, install, test and commission to the satisfaction of the Engineer the following including builders' works
WATER STORAGE
A | Cold water sectional tank as GRP, size 5m x 4m x 1m high, Capacity: 20,000 litres, to be installed on the Structural Tower, complete with 40mm washout, 25mm overflow, 25mm inlet and 80mm outlet | No | 1
B | Allow for emptying the existing 10,000 litres water tank, disconecting it and handing it over to the Client | Item | 1
C | Apply to NW&SC and allow for upgrading the existing 20mm water connection to a 25mm connection complete with a meter. The upgrade shall be instructed by the Mechanical Engineer if the required flowrate to the new elevated storage tank is not suitable. | Item | 1 |  |  | 0
D | 2. Apply to Jinja Authority and allow for opening up and making good the Road to replace the underground incoming water supply line. The works shall be carried out to the Authority’s requirements and approval. | Item | 1 |  |  | 0
E | Uninstall one of the stand pipes next to the Building and re-install test and commission at an agreed location with a concrete base and soak away complete with a water connection and all necessary accessories | Item | 1
RISING MAIN
F | HDPE 25mm distribution pipe complete with all necessary fittings, clamps and including builders works to be laid in trench as rising main to cold water storage tank Tower | m | 120
G | Control valves for cold water pipes, size 25mm as per drawings | No. | 2
H | Allow for making a new water connection to the existing washrooms | Item | 1
I | Allow for careful decommissioning of the existing water pump and handover to the Client | Item | 1
TOTAL TO COLLECTION
RISK WORKS (Cont'd)
DRAINAGE SYSTEM - PIPES AND FITTINGS
All pipes and fittings are to Terrain manufacture unless otherwise specified. The pipes and fittings are to be fitted complete with all necessary fittings and accessories including clamps and all builders work
A | Excavate for and construct manhole size 450 x 600mm and not exceeding 1m deep including channels, benching and providing medium duty cast iron manhole cover and frame to Structural Engineer's detail | No | 4
B | Excavate for and construct manhole size 450 x 600mm and not exceeding 1m deep including channels, benching and Re-using the existing manhole cover and frame | No | 4
C | Excavate and fill with gravel Soak pits 2m diameter x 2m deep complete to SE detail | No. | 1
TOTAL TO COLLECTION
RISK WORKS COLLECTION
PAGE M1
PAGE M2
TOTAL TO COLLECTION

## Summary
COMPLETION OF COFFEE ANALYTICAL LABARATORY & REGIONAL OFFICE AT RUKOKI KASESE.
MECHANICAL INSTALLATION - BILL OF QUANTITIES
Item | Description & Specification | Page | Amount (UGX)
MAIN SUMMARY PAGE
| PLUMBING INSTALLATIONS | P-T
| FIRE FIGHTING INSTALLATIONS | FF -T
| AIR CONDITIONING AND VENTILATION | VAC-T
TOTAL FOR MECHANICAL INSTALLATION